## Slide 1: Introduction to Optimization and Application to Economic Dispatch and Unit Commitment
Daniel Kirschen

## Slide 2: Perspective
Conventional PS economics problems:
  Economic Dispatch (ED)
  Unit Commitment (UC)
  Optimal Power Flow (OPF)
Assume monopoly, vertically integrated utility
Why?
  Conceptually simpler
  Variants for competitive electricity markets
  Comparison with “benevolent monopolist”

## Slide 3: Economic dispatch problem
Several generating units serving the load
What share of the load should each generating unit produce?
Consider the limits of the generating units
Ignore the limits of the network
A
B
C
L

## Slide 4: Types of Power Plants
Thermal power plants
Renewable energy sources
Hydro power plants

## Slide 5: Thermal power plants
  Burn a fuel to generate electric power
  Coal, oil, gas, biomass, uranium, ..
Economic characteristics:
  Substantial operating cost
  On/off status and power output can be changed
    Within limits
Nuclear units:
  Low operating cost but very limited flexibility
Typically multiple units in a power plant

## Slide 6: Renewable energy sources
Wind, solar, geothermal, tidal
Economic characteristics:
  Negligible operating cost
  Intermittent (except geothermal)
  Stochastic (wind, solar)
  High investment cost per kW of capacity
  Use it or lose it

## Slide 7: Hydro power plants
Economic characteristics
  Negligible operating cost
  Storage capability
Hydro with reservoir
  Controllable output
  Size of the reservoir is highly variable
    Days to years
“Run of the river” hydro
  No reservoir or negligible reservoir
  Uncontrollable output: use it or lose it

## Slide 8: Concept of net load
actual load – uncontrolled renewable generation
= net load
= controllable generation
-
=
We’ll assume that the uncontrollable renewable generation is known and dispatch the controllable generation to meet the net load
Notes: Northwest Power and Conservation Counci

## Slide 9: Hydro-thermal coordination
Q: Would you rather generate a MWh using hydro or thermal generation?
A: It depends..
  If there is a reservoir (and it is not full) a MWh from hydro can be generated now or later
  It may have more value later, depending on how much the thermal MWh costs now and later
We will assume that the hydro production is given

## Slide 10: Characteristics of the thermal units
Thermal generating units
Consider the running costs only
Input / Output curve
  Fuel vs. electric power
Fuel consumption measured by its energy content
Upper and lower limit on output of the generating unit
B
T
G
(Input)
Electric Power
Fuel
(Output)
Output
Pmin
Pmax
Input
J/h
MW

## Slide 11: Cost Curve
Multiply fuel input by fuel cost
No-load cost
  Cost of keeping the unit running if it could produce zero MW
Output
Pmin
Pmax
Cost
$/h
MW
No-load cost

## Slide 12: Incremental Cost Curve
Incremental cost curve
Derivative of the cost curve
In $/MWh
Cost of the next MWh
∆F
∆P
Cost [$/h]
MW
Incremental Cost
[$/MWh]
MW

## Slide 13: Mathematical formulation
Objective: Minimize
Constraints
  Load / Generation balance:
  Unit Constraints:
A
B
C
L
This is an optimization problem

## Slide 14: Introduction to Optimization

## Slide 15: Objective
Achieving the best possible design or operating conditions requires a way of measuring the goodness of this result
We will call this measure our objective F
Examples:
  minimize cost of building a transformer
  minimize cost of supplying power
  minimize losses in a power system
  maximize profit from a bidding strategy

## Slide 16: Decision Variables
The value of the objective is a function of some decision variables:
Examples of decision variables:
  Dimensions of the transformer
  Output of generating units, position of taps
  Parameters of bids for selling electrical energy

## Slide 17: Optimization Problem
What value should the decision variables take so that is minimum or maximum?

## Slide 18: Example: function of one variable
x
f(x)
x*
f(x*)
f(x) is maximum for x = x*

## Slide 19: Minimization and Maximization
x
f(x)
x*
f(x*)
If x = x* maximizes f(x) then it minimizes - f(x)
-f(x)
-f(x*)

## Slide 20: Minimization and Maximization
Maximizing f(x) is thus the same thing as minimizing g(x) = -f(x)
Minimization and maximization problems are thus interchangeable
Depending on the problem, the optimum is either a maximum or a minimum

## Slide 21: Necessary Condition for Optimality
x
f(x)
x*
f(x*)

## Slide 22: Necessary Condition for Optimality
x
f(x)
x*

## Slide 23: Example
x
f(x)
For what values of x is ?
In other words, for what values of x is the necessary condition for optimality satisfied?

## Slide 24: Example
A, B, C, D are stationary points
A and D are maxima
B is a minimum
C is an inflexion point
x
f(x)
A
B
C
D

## Slide 25: How can we distinguish minima and maxima?
x
f(x)
A
B
C
D
The objective function is concave around a maximum

## Slide 26: How can we distinguish minima and maxima?
x
f(x)
A
B
C
D
The objective function is convex around a minimum

## Slide 27: How can we distinguish minima and maxima?
x
f(x)
A
B
C
D
The objective function is flat around an inflexion point

## Slide 28: Necessary and Sufficient Conditions of Optimality
Necessary condition:
Sufficient condition:
  For a maximum:
  For a minimum:

## Slide 29: Isn’t all this obvious?
Can’t we tell all this by looking at the objective function?
  Yes, for a simple, one-dimensional case when we know the shape of the objective function
  For complex, multi-dimensional cases (i.e. with many decision variables) we can’t visualize the shape of the objective function
  We must then rely on mathematical techniques

## Slide 30: Feasible Set
The values that the decision variables can take are usually limited
Examples:
  Physical dimensions of a transformer must be positive
  Active power output of a generator may be limited to a certain range (e.g. 200 MW to 500 MW)
  Reactive power output of a generator may be limited to a certain range (e.g. -100 MVAr to 150 MVAr)

## Slide 31: Feasible Set
x
f(x)
A
D
xMAX
xMIN
Feasible Set
The values of the objective function outside
the feasible set do not matter

## Slide 32: Two-Dimensional Case
x1
x2
f(x1,x2)
x2*
x1*
f(x1,x2) is minimum for x1*, x2*

## Slide 33: Necessary Conditions for Optimality
x1
x2
f(x1,x2)
x2*
x1*

## Slide 34: Multi-Dimensional Case
At a maximum or minimum value of
we must have:
A point where these conditions are satisfied is called a stationary point

## Slide 35: Sufficient Conditions for Optimality
x1
x2
f(x1,x2)
minimum
maximum

## Slide 36: Sufficient Conditions for Optimality
x1
x2
f(x1,x2)
Saddle point

## Slide 37: Sufficient Conditions for Optimality
Calculate the Hessian matrix at the stationary point:

## Slide 38: Sufficient Conditions for Optimality
Calculate the eigenvalues of the Hessian matrix at the stationary point
If all the eigenvalues are greater or equal to zero:
  The matrix is positive semi-definite
  The stationary point is a minimum
If all the eigenvalues are less or equal to zero:
  The matrix is negative semi-definite
  The stationary point is a maximum
If some or the eigenvalues are positive and other are negative:
  The stationary point is a saddle point

## Slide 39: Calculating eigenvalues
The eigenvalues of a matrix A are such that:
Where I is the identity matrix:

## Slide 40: Contours
x1
x2
f(x1,x2)
F1
F2
F2
F1

## Slide 41: Contours
x1
x2
Minimum or maximum
A contour is the locus of all the point that give the same value to the objective function

## Slide 42: Example 1
is a stationary point

## Slide 43: Example 1
Sufficient conditions for optimality:
must be positive definite (i.e. all eigenvalues must be positive)
The stationary point
is a minimum

## Slide 44: Example 1
x1
x2
C=1
C=4
C=9
Minimum: C=0

## Slide 45: Example 2
is a stationary point

## Slide 46: Example 2
Sufficient conditions for optimality:
The stationary point
is a saddle point

## Slide 47: Example 2
x1
x2
C=1
C=4
C=9
C=1
C=4
C=9
C=-1
C=-4
C=-9
C=0
C=0
C=-9
C=-4
This stationary point is a saddle point

## Slide 48: In practice..
In practice we don’t check the sufficient conditions for optimality
If the problem is convex a stationary point will be a minimum
Or we rely on the nature of the problem to “ensure” that a stationary point will be a minimum or a maximum

## Slide 49
Optimization with Constraints

## Slide 50: Optimization with Equality Constraints
There are usually restrictions on the values that the decision variables can take
Objective function
Equality constraints

## Slide 51: Number of Constraints
N decision variables
M equality constraints
If M > N, the problems is over-constrained
  There is usually no solution
If M = N, the problem is determined
  There may be a solution
If M < N, the problem is under-constrained
  There is usually room for optimization

## Slide 52: Example 1
x1
x2
Minimum

## Slide 53: Example 2: Economic Dispatch
L
G1
G2
x1
x2
Cost of running unit 1
Cost of running unit 2
Total cost
Optimization problem:

## Slide 54: Solution by substitution
Unconstrained minimization

## Slide 55: Solution by substitution
Difficult
Usually impossible when constraints are non-linear
Provides little or no insight into solution
 Solution using Lagrange multipliers

## Slide 56: Gradient

## Slide 57: Properties of the Gradient
Each component of the gradient vector indicates the rate of change of the function in that direction
The gradient indicates the direction in which a function of several variables increases most rapidly
The magnitude and direction of the gradient usually depend on the point considered
At each point, the gradient is perpendicular to the contour of the function

## Slide 58: Example 3
x
y

## Slide 59: Example 4
x
y

## Slide 60: Lagrange multipliers

## Slide 61: Lagrange multipliers

## Slide 62: Lagrange multipliers

## Slide 63: Lagrange multipliers
The solution must be on the constraint
To reduce the value of f, we must move in a direction opposite to the gradient

## Slide 64: Lagrange multipliers
We stop when the gradient of the function is perpendicular to the constraint because moving further would increase the value of the function
At the optimum, the gradient of the function is parallel to the gradient of the constraint

## Slide 65: Lagrange multipliers
At the optimum, we must have:
Which can be expressed as:
is called the Lagrange multiplier
The constraint must also be satisfied:
In terms of the co-ordinates:

## Slide 66: Lagrangian function
To simplify the writing of the conditions for optimality, it is useful to define the Lagrangian function:
The necessary conditions for optimality are then given by the partial derivatives of the Lagrangian:

## Slide 67: Example

## Slide 68: Example

## Slide 69: Example
x1
x2
Minimum
4
1

## Slide 70: Important Note!
If the constraint is of the form:
It must be included in the Lagrangian as follows:
And not as follows:

## Slide 71: Application to Economic Dispatch
L
G1
G2
x1
x2
Equal incremental cost solution

## Slide 72: Incremental Cost
x1
x2
x1
x2
Cost curves:
Incremental cost curves:

## Slide 73: Interpretation of this solution
x1
x2
L
+
-
-
If < 0, reduce λ
If > 0, increase λ

## Slide 74: Physical interpretation
x
x
The incremental cost is the cost of one additional MW for one hour.
This cost depends on the output of
the generator.

## Slide 75: Physical interpretation

## Slide 76: Physical interpretation
It pays to increase the output of unit 2 and decrease the output of unit 1 until we have:
The Lagrange multiplier λ is thus the cost of one more MW at the optimal solution.
This is a very important result with many applications in
economics.

## Slide 77: Generalization
Lagrangian:
One Lagrange multiplier for each constraint
n + m variables: x1, …, xn and λ1, …, λm

## Slide 78: Optimality conditions
n equations
m equations
n + m equations in
n + m variables

## Slide 79: Optimization with inequality constraints
Objective function
Equality constraints
Inequality constraints

## Slide 80: Example: Economic Dispatch
L
G1
G2
x1
x2
Inequality constraints
Equality constraints

## Slide 81: Example: Economic Dispatch
x1
x2
Family of ellipses
x1max
x1min
x2min
x2max
A
Ellipse tangent to equality constraint at A
Inequality constraints are satisfied

## Slide 82: Example: Economic Dispatch
x1
x2
x1max
x1min
x2min
x2max
A
Ellipse tangent to equality constraint at B
Inequality constraints are NOT satisfied!
What is the solution for a larger load?
B

## Slide 83: Example: Economic Dispatch
x1
x2
x1max
x1min
x2min
x2max
A
C is the solution because it is the point on the equality constraint that satisfies the inequality constraints at minimum cost
B
C

## Slide 84: Binding Inequality Constraints
A binding inequality constraint is an inequality constraint that is satisfied exactly
Example:
  If we must have x1 ≤ x1max
  And at the solution we have x1 = x1max
  Then the constraint x1 ≤ x1max is said to be binding
ALL of the inequality constraints must be satisfied
Only a FEW will be binding (or active) at any given time
But we don’t know ahead of time which inequality constraints will be binding!
All equality constraints are always binding

## Slide 85: Solution using Lagrange multipliers
Lagrangian function:

## Slide 86: Optimality Conditions
Complementary Slackness Conditions
(Known as the Karush Kuhn Tucker (KKT) conditions

## Slide 87: Complementary slackness conditions
Two possibilities for each constraint j:
OR

## Slide 88: Warning!
Difficulty with the complementary slackness conditions
  They tell us that an inequality constraint is either binding or non-binding
  They DON’T tell us which constraints are binding and non-binding
  The binding constraints have to be identified through trial and error

## Slide 89: Example

## Slide 90: Example
x1
x2

## Slide 91: Example

## Slide 92: Example
KKT conditions do not tell us if inequality constraint is binding
Must use a trial and error approach
Trial 1: Assume inequality constraint is not binding μ = 0
From solution of example without inequality constraint, we know that the solution is then:
This solution is thus not an acceptable solution

## Slide 93: Example
Trial 2: Assume that the inequality constraint is binding
All KKT conditions are satisfied. This solution is acceptable

## Slide 94: Example: graphical solution
x1
x2
Solution of problem with inequality constraint
Solution of problem without inequality constraint
Solution of problem without constraints

## Slide 95: Application to Economic Dispatch
L
G1
G2
x1
x2

## Slide 96: Application to Economic Dispatch
KKT Conditions:

## Slide 97: Application to Economic Dispatch
KKT Conditions (continued):

## Slide 98: Solving the KKT Equations
Case #1: No generator is at a limit
No inequality constraint is binding and all μ’s are equal to zero
All generators operate at the same incremental cost

## Slide 99: Solving the KKT Equations
Case #2: Generator 1 is at its upper limit; Other limits not binding
All generators do NOT operate at the same incremental cost!
The incremental cost of unit 1 is lower…. Why?
If that was possible, more power would be produced by unit 1

## Slide 100: Solving the KKT Equations
Case #3: Generator 1 is at its lower limit; other limits not binding
Again, all generators do NOT operate at the same incremental cost!
The incremental cost of unit 1 is higher… Why?
If that was possible, less power would be produced by unit 1

## Slide 101: Physical Interpretation of Lagrange Multipliers
= 0
= 0
Marginal cost of equality constraint
Marginal cost of inequality constraint

## Slide 102: Physical Interpretation of Lagrange Multipliers
Constraints always increase the cost of a solution
The Lagrange multipliers give the incremental cost of the binding constraints at the optimum
They are sometimes called shadow costs
Non-binding inequality constraints have a zero incremental cost

## Slide 103: Economic Dispatch
Example of Calculation Using Lagrange Multipliers

## Slide 104: Economic Dispatch Example
A load of 800 MW is supplied by three generating units.
The cost characteristics of these generating units are
given by the following expressions:
C1 = 100 + 8 P1 + 0.1 P12 [$/h] 230 ≤ P1 ≤ 400 MW
C2 = 200 + 7 P2 + 0.06 P22 [$/h] 100 ≤ P2 ≤ 500 MW
C3 = 250 + 9 P3 + 0.07 P32 [$/h] 100 ≤ P3 ≤ 260 MW
Calculate the optimal economic dispatch.

## Slide 105: Example: Form the Lagrangian

## Slide 106: Example: Optimality Conditions
Set the partial derivatives of the Lagrangian with respect to the decision variables and λ to zero:
(1)
(2)
(3)
(4)

## Slide 107: Example: Optimality Conditions
Set the partial derivatives of the Lagrangian with respect to the μ’s to zero:

## Slide 108: Example: Optimality Conditions
Set the partial derivatives of the Lagrangian with respect to the μ’s to zero:

## Slide 109: Example: Complementary slackness

## Slide 110: Example: First Trial (1)
Assume that none of the inequality constraints is binding
This means that all the μ‘s are zero
Set the μ’s equal to zero in the optimality conditions.
Equations (1) to (3) become:

## Slide 111: Example: First Trial (2)
Inserting these expressions in Equation (4), we get:
With L = 800MW, we get:
Replacing λ in the equations on the previous slide, we have:
Not a valid solution
 trial fails

## Slide 112: Example: Second Trial (1)
We must try another combination of binding constraints.
Let us try:
6 inequality constraints  26 = 64 possible combinations
Realistic system  ridiculously large number of combinations
Must use information from previous trials

## Slide 113: Example: Second Trial (2)
However, we must check that the μ‘s meet the complementary slackness conditions

## Slide 114: Example: Second Trial (3)

## Slide 115: Example: Second Trial (4)
The constraint
should not be binding!
What is happening?
First trial:

## Slide 116: Example: Second Trial (5)
Second trial:
In the second trial, we “pushed” P1 towards its lower limit and P3 towards its upper limit. However, there was no need to push P3 because increasing P1 would naturally reduce P3 below its limit.

## Slide 117: Example: Third Trial (1)

## Slide 118: Example: Third Trial (2)
Solution that satisfies all the optimality conditions:
 Cost of an extra MW of load
 Value of reducing by 1MW

## Slide 119: Example: Optimal Solution
Third trial:

## Slide 120: Practical Economic Dispatch

## Slide 121: Equal Incremental Cost Dispatch
PA
PB
PC
+

## Slide 122: Lambda search algorithm

## Slide 123: Linear Cost Curves
PA
PB
PAMAX
PBMAX
PA
PB
PAMAX
PBMAX

## Slide 124: Linear Cost Curves
PA
PB
PA
PB
PAMAX
PBMAX
PAMAX
PBMAX

## Slide 125: Linear Cost Curves
PA
PB
PA
PB
PAMAX
PBMAX
PAMAX
PBMAX

## Slide 126: Linear Cost Curves
The output of the unit with the lowest incremental cost (in this case unit A) is increased first (it is “loaded” first)
The output of the other units is not increased until unit A is loaded up to its maximum
The output of the unit with second lowest incremental cost is then increased (i.e. the “second cheapest” unit)
And so on until the generation meets the load

## Slide 127: Linear cost curves with minimum generation
PA
PB
PA
PB
PAMAX
PBMAX
PBMIN
PAMIN
PAMAX
PBMAX
PBMIN
PAMIN

## Slide 128: Linear cost curves with minimum generation
All generating units are first loaded up to their minimum generation
The generating units are then loaded in order of incremental cost

## Slide 129: Piecewise Linear Cost Curves
PA
PB
PA
PB

## Slide 130: Economic Dispatch with Piecewise Linear Cost Curves
PA
PB
PA
PB

## Slide 131: Economic Dispatch with Piecewise Linear Cost Curves
PA
PB
PA
PB

## Slide 132: Economic Dispatch with Piecewise Linear Cost Curves
PA
PB
PA
PB

## Slide 133: Economic Dispatch with Piecewise Linear Cost Curves
PA
PB
PA
PB

## Slide 134: Economic Dispatch with Piecewise Linear Cost Curves
PA
PB
PA
PB

## Slide 135: Economic Dispatch with Piecewise Linear Cost Curves
All generators except one are at breakpoints of their cost curve
The marginal generator is between breakpoints to balance the load and generation
Not well-suited for lambda-search algorithm
Very fast table lookup algorithm:
  Rank all the segments of the piecewise linear cost curves in order of incremental cost
  First dispatch all the units at their minimum generation
  Then go down the table until the generation matches the load

## Slide 136: Example
PA
PB
20
30
70
80
110
120
140
150
0.1
0.6
0.8
0.3
0.5
0.7
If Pload = 210MW
The optimal economic dispatch is:
PA = 120MW
PB = 90 MW
λ = 0.6

## Slide 137: Local and Global Optima

## Slide 138: Which one is the real maximum?
x
f(x)
A
D

## Slide 139: Which one is the real optimum?
x1
x2
B
A
C
D

## Slide 140: Local and Global Optima
The optimality conditions are local conditions
They do not compare separate optima
If I find an optimum can I be sure that it is the global optimum?
In general, to find the global optimum, we must find and compare all the optima
In large problems, this can be very difficult and time consuming

## Slide 141: Convexity
If the feasible set is convex and the objective function is convex, there is only one minimum and it is thus the global minimum

## Slide 142: Examples of Convex Feasible Sets
x1
x2
x1
x2
x1
x1
x2
x1min
x1max

## Slide 143: Example of Non-Convex Feasible Sets
x1
x2
x1
x2
x1
x2
x1
x1a
x1d
x1b
x1c
x1

## Slide 144: Example of Convex Feasible Sets
x1
x2
x1
x2
x1
x2
A set is convex if, for any two points belonging to the set, all the points on the straight line joining these two points belong to the set
x1
x1min
x1max

## Slide 145: Example of Non-Convex Feasible Sets
x1
x2
x1
x2
x1
x2
x1
x1a
x1d
x1b
x1c
x1

## Slide 146: Example of Convex Function
x
f(x)

## Slide 147: Example of Convex Function
x1
x2

## Slide 148: Example of Non-Convex Function
x
f(x)

## Slide 149: Example of Non-Convex Function
x1
x2
B
A
C
D

## Slide 150: Definition of a Convex Function
x
f(x)
xa
xb
y
f(y)
z
A convex function is a function such that, for any two points xa and xb belonging to the feasible set and any k such that 0 ≤ k ≤1, we have:

## Slide 151: Example of Non-Convex Function
x
f(x)

## Slide 152: Importance of Convexity
If we can prove that a minimization problem is convex:
  Convex feasible set
  Convex objective function
Then, the problem has one and only one solution
Proving convexity is often difficult
Power system problems are usually not convex
There may be more than one solution to power system optimization problems

## Slide 153: Unit Commitment
Daniel Kirschen

## Slide 154: Economic Dispatch: Problem Definition
Given load
Given set of units on-line
How much should each unit generate to meet this load at minimum cost?
A
B
C
L

## Slide 155: Unit Commitment
Given load profile (e.g. values of the load for each hour of a day)
Given set of units available
When should each unit be started, stopped and how much should it generate to meet the load at minimum cost?
G
G
G
Load Profile
?
?
?

## Slide 156: Typical summer and winter loads

## Slide 157: A Simple Example
Unit 1:
    PMin = 250 MW, PMax = 600 MW
    C1 = 510.0 + 7.9 P1 + 0.00172 P12 $/h
Unit 2:
    PMin = 200 MW, PMax = 400 MW
    C2 = 310.0 + 7.85 P2 + 0.00194 P22 $/h
Unit 3:
    PMin = 150 MW, PMax = 500 MW
    C3 = 78.0 + 9.56 P3 + 0.00694 P32 $/h
What combination of units 1, 2 and 3 will produce 550 MW at minimum cost?
How much should each unit in that combination generate?

## Slide 158: Cost of the various combinations

## Slide 159: Observations on the example:
Far too few units committed: Can’t meet the demand
Not enough units committed: Some units operate above optimum
Too many units committed: Some units below optimum
Far too many units committed: Minimum generation exceeds demand

## Slide 160: Effect of the no-load cost
Example:
Economic dispatch looks only at marginal cost:
This example considered the total cost
The no-load cost affects the solution
No-load cost

## Slide 161: Another Example
Optimal generation schedule for a load profile
Decompose the profile into a set of period
Assume load is constant over each period
For each time period, which units should be committed to generate at minimum cost during that period?
Load
Time
12
6
0
18
24
500
1000

## Slide 162: Optimal combination for each hour

## Slide 163: Matching the combinations to the load
Load
Time
12
6
0
18
24
Unit 1
Unit 2
Unit 3

## Slide 164: Unit commitment as an optimization problem
Minimize total cost over time horizon
  Total cost = running cost + startup cost
Constraints
  Unit constraints
  System constraints
Time horizon is divided in a set of optimization periods:
During each period:
  The load is assumed constant
  The decision variables are constant

## Slide 165: Notations
Status of unit i at period t
Power produced by unit i during period t
Unit i is ON during period t
Unit i is OFF during period t
Running cost of unit i during period t
Startup cost of unit i during period t
Number of available generating units
Number of periods in the optimization horizon

## Slide 166: Running cost
Cost of generating power with a given unit
Depends on the power output of the unit
Same cost function as used in economic dispatch
Includes the no-load cost

## Slide 167: Start-up cost
Thermal generating units:
  Coal, gas, oil, biomass
These units must be “warmed up” before they can be brought on-line
Warming up a unit requires fuel and therefore costs money
Incurred only during the first period when the unit is turned on

## Slide 168: Start-up cost
Start-up cost depends on time unit has been off
  If the unit has not been off for a long time, the water will still be warm
  Hot start vs. cold start
tiOFF
αi
αi + βi

## Slide 169: Effect of the start-up cost
Need to “balance” start-up costs and running costs
Example:
  Diesel generator: low start-up cost, high running cost
  Coal plant: high start-up cost, low running cost
Issues:
  How long should a unit run to “recover” its start-up cost?
  Start-up one more large unit or a diesel generator to cover the peak?
  Shutdown one more unit at night or run several units part-loaded?

## Slide 170: Objective function
Running cost
Startup cost
Decision
variables

## Slide 171: Unit Constraints
Constraints that affect each unit individually:
  Maximum generating capacity
  Minimum stable generation
  Minimum “up time”
  Minimum “down time”
  Ramp rate

## Slide 172: Unit Constraints
Minimum up time
  Once a unit is running it may not be shut down immediately:
Minimum down time
  Once a unit is shut down, it may not be started immediately

## Slide 173: Unit Constraints
Maximum ramp rates
  To avoid damaging the turbine, the electrical output of a unit cannot change by more than a certain amount over a period of time:
Maximum ramp up rate constraint:
Maximum ramp down rate constraint:

## Slide 174: System Constraints
Constraints that affect more than one unit
  Load/generation balance
  Reserve generation capacity
  Emission constraints
  Network constraints

## Slide 175: Load/Generation Balance Constraint
At all times, the power produced by the generating
units must be equal to the load

## Slide 176: Reserve Constraint
Unanticipated loss of a generating unit or an interconnection causes unacceptable frequency drop if not corrected
Need to increase production from other units to keep frequency drop within acceptable limits
Rapid increase in production only possible if committed units are not all operating at their maximum capacity
Some of the capacity of the generating units must be kept “in reserve”

## Slide 177: Reserve Constraint
Contribution of unit i to reserve at period t (“headroom”)
Load generation balance
Reserve requirement at period t
Reserve constraint at period t

## Slide 178: How much reserve?
Protect the system against “credible outages”
Reserve requirement:
  Capacity of largest unit or interconnection
  Percentage of peak load

## Slide 179: Types of Reserve
Spinning reserve
  Primary
    Quick response for a short time
  Secondary
    Slower response for a longer time
Tertiary reserve
  Replace primary and secondary reserve to protect against another outage
  Provided by units that can start quickly
    e.g. gas turbines
  Also called scheduled or off-line reserve

## Slide 180: Cost of Reserve
Reserve has a cost even when it is not called
  More units scheduled than required
    Units not operated at their maximum efficiency
    Extra start up costs
  Must build units capable of rapid response
  Cost of reserve proportionally larger in small systems
    Important driver for the creation of interconnections between systems

## Slide 181: Emission Constraints
Amount of pollutants that generating units can emit may be limited
Pollutants:
  SO2, NOx
Various forms:
  Limit on each plant at each hour
  Limit on plant over a year
  Limit on a group of plants over a year
  Etc…

## Slide 182: Network Constraints
Transmission network may have an effect on the commitment of units
  Some units must run to provide voltage support
  The output of some units may be limited because their output would exceed the transmission capacity of the network
Cheap generators
May be “constrained off”
More expensive generator
May be “constrained on”
A
B

## Slide 183: Why can’t we treat each period separately?
Large units are efficient but have a substantial startup cost
  Need to “amortize” this startup cost over the optimization horizon
Some constraints create a link between the periods
  Minimum up- and down-time constraint
  Ramping constraints

## Slide 184: Economic Dispatch vs. Unit Commitment
Generation scheduling or unit commitment is a more general problem than economic dispatch
Economic dispatch is a sub-problem of generation scheduling
Unit commitment must strike a balance between cheaper inflexible units and more expensive flexible units

## Slide 185: Flexible Plants
Power output can be adjusted (within limits)
Examples:
  Coal-fired
  Oil-fired
  Open cycle gas turbines
  Combined cycle gas turbines
  Hydro plants with storage
Status and power output can be optimized
Thermal units

## Slide 186: Inflexible Plants
Power output cannot be adjusted for technical or commercial reasons
Examples:
  Nuclear
  Run-of-the-river hydro
  Renewables (wind, solar,…)
  Combined heat and power (CHP, cogeneration)
Output treated as given when optimizing

## Slide 187: Solving the Unit Commitment Problem
Decision variables:
  Status of each unit at each period:
  Output of each unit at each period:
Combination of integer and continuous variables

## Slide 188: Optimization with integer variables
Continuous variables
  Can follow the gradients or use LP
  Any value within the feasible set is OK
Discrete variables
  There is no gradient
  Can only take a finite number of values
  Problem is not convex
  Must try combinations of discrete values

## Slide 189: How many combinations are there?
Examples
  3 units: 8 possible states
  N units: 2N possible states
111
110
101
100
011
010
001
000

## Slide 190: How many solutions are there anyway?
1
2
3
4
5
6
T=
Optimization over a time horizon divided into intervals
A solution is a path linking one combination at each interval
How many such paths are there?

## Slide 191: How many solutions are there anyway?
1
2
3
4
5
6
T=
Optimization over a time horizon divided into intervals
A solution is a path linking one combination at each interval
How many such path are there?
Answer:

## Slide 192: The Curse of Dimensionality
Example: 5 units, 24 hours
Processing 109 combinations/second, this would take 1.9 1019 years to solve
There are 100’s of units in large power systems...
Many of these combinations do not satisfy the constraints

## Slide 193: How do you Beat the Curse?
Brute force approach won’t work!
Need to be smart
Try only a small subset of all combinations
Can’t guarantee optimality of the solution
Try to get as close as possible within a reasonable amount of time

## Slide 194: Main Solution Techniques
Characteristics of a good technique
  Solution close to the optimum
  Reasonable computing time
  Ability to model constraints
Possible techniques
  Priority list / heuristic approach
  Dynamic programming
  Lagrangian relaxation
  Mixed Integer Programming
Heuristic techniques (e.g particle swarm optimization) are a waste of time
State of the art

## Slide 195: A Simple Unit Commitment Example

## Slide 196: Unit Data
Unit | Pmin (MW) | Pmax (MW) | Min up (h) | Min down (h) | No-load cost ($) | Marginal cost ($/MWh) | Start-up cost ($) | Initial status
A | 150 | 250 | 3 | 3 | 0 | 10 | 1,000 | ON
B | 50 | 100 | 2 | 1 | 0 | 12 | 600 | OFF
C | 10 | 50 | 1 | 1 | 0 | 20 | 100 | OFF

## Slide 197: Cost curves
p
C(p)
A
B
C

## Slide 198: Demand Data
Reserve requirements are not considered

## Slide 199: Feasible Unit Combinations (states)
Combinations |  |  | Pmin | Pmax
A | B | C |  | 
1 | 1 | 1 | 210 | 400
1 | 1 | 0 | 200 | 350
1 | 0 | 1 | 160 | 300
1 | 0 | 0 | 150 | 250
0 | 1 | 1 | 60 | 150
0 | 1 | 0 | 50 | 100
0 | 0 | 1 | 10 | 50
0 | 0 | 0 | 0 | 0
 | 1 | 2 | 3
 | 150 | 300 | 200

## Slide 200: Transitions between feasible combinations
A | B | C
1 | 1 | 1
1 | 1 | 0
1 | 0 | 1
1 | 0 | 0
0 | 1 | 1
 | 1 | 2 | 3
Initial State

## Slide 201: Infeasible transitions: Minimum down time of unit A
A | B | C
1 | 1 | 1
1 | 1 | 0
1 | 0 | 1
1 | 0 | 0
0 | 1 | 1
 | 1 | 2 | 3
Initial State
 | TD | TU
A | 3 | 3
B | 1 | 2
C | 1 | 1

## Slide 202: Infeasible transitions: Minimum up time of unit B
A | B | C
1 | 1 | 1
1 | 1 | 0
1 | 0 | 1
1 | 0 | 0
0 | 1 | 1
 | 1 | 2 | 3
Initial State
 | TD | TU
A | 3 | 3
B | 1 | 2
C | 1 | 1

## Slide 203: Feasible transitions
A | B | C
1 | 1 | 1
1 | 1 | 0
1 | 0 | 1
1 | 0 | 0
0 | 1 | 1
 | 1 | 2 | 3
Initial State

## Slide 204: Operating costs
1 | 1 | 1
1 | 1 | 0
1 | 0 | 1
1 | 0 | 0
1
4
3
2
5
6
7

## Slide 205: Economic dispatch
State | Load | PA | PB | PC | Cost
1 | 150 | 150 | 0 | 0 | 1500
2 | 300 | 250 | 0 | 50 | 3500
3 | 300 | 250 | 50 | 0 | 3100
4 | 300 | 240 | 50 | 10 | 3200
5 | 200 | 200 | 0 | 0 | 2000
6 | 200 | 190 | 0 | 10 | 2100
7 | 200 | 150 | 50 | 0 | 2100
Unit | Pmin | Pmax | No-load cost | Marginal cost
A | 150 | 250 | 0 | 10
B | 50 | 100 | 0 | 12
C | 10 | 50 | 0 | 20

## Slide 206: Operating costs
1 | 1 | 1
1 | 1 | 0
1 | 0 | 1
1 | 0 | 0
1
4
3
2
5
6
7
$1500
$3500
$3100
$3200
$2000
$2100
$2100

## Slide 207: Start-up costs
1 | 1 | 1
1 | 1 | 0
1 | 0 | 1
1 | 0 | 0
1
4
3
2
5
6
7
$1500
$3500
$3100
$3200
$2000
$2100
$2100
Unit | Start-up cost
A | 1000
B | 600
C | 100
$0
$0
$0
$0
$0
$600
$100
$600
$700

## Slide 208: Accumulated costs
1 | 1 | 1
1 | 1 | 0
1 | 0 | 1
1 | 0 | 0
1
4
3
2
5
6
7
$1500
$3500
$3100
$3200
$2000
$2100
$2100
$1500
$5100
$5200
$5400
$7300
$7200
$7100
$0
$0
$0
$0
$0
$600
$100
$600
$700

## Slide 209: Total costs
1 | 1 | 1
1 | 1 | 0
1 | 0 | 1
1 | 0 | 0
1
4
3
2
5
6
7
$7300
$7200
$7100
Lowest total cost

## Slide 210: Optimal solution
1 | 1 | 1
1 | 1 | 0
1 | 0 | 1
1 | 0 | 0
1
2
5
$7100

## Slide 211: Notes
This example is intended to illustrate the principles of unit commitment
Some constraints have been ignored and others artificially tightened to simplify the problem and make it solvable by hand
Therefore it does not illustrate the true complexity of the problem
The solution method used in this example is based on dynamic programming. This technique is no longer used in industry because it only works for small systems (< 20 units)

## Slide 212: Linear Programming (LP)

## Slide 213: Motivation
Many optimization problems are linear
  Linear objective function
  All constraints are linear
Non-linear problems can be linearized:
  Piecewise linear cost curves
  DC power flow
Efficient and robust method to solve such problems

## Slide 214: Piecewise linearization of a cost curve
PA

## Slide 215: Mathematical formulation
n
minimize Σ cj xj
j =1
n
subject to: Σ aij xj ≤ bi, i = 1, 2, . . ., m
j =1
n
Σ hij xj = di, i = 1, 2, . . ., p
j =1
Decision variables: xj
Constants: cj, aij, bi, hij, di

## Slide 216: Example 1
x
3
0
1
2
y
0
1
2
4
3
Feasible Region
x + 2 y ≥ 2
y ≤ 4
x ≤ 3
x ≥ 0; y ≥ 0
Subject to:
Maximize x + y
Example borrowed from Piyush Kumar of Florida State University)

## Slide 217: Example 1
x
3
0
1
2
y
0
1
2
4
3
x + 2 y ≥ 2
y ≤ 4
x ≤ 3
x ≥ 0; y ≥ 0
Subject to:
Maximize x + y
x + y = 0

## Slide 218: Example 1
x
3
0
1
2
y
0
1
2
4
3
Maximize x + y
x + y = 1
Feasible Solution
x + 2 y ≥ 2
y ≤ 4
x ≤ 3
x ≥ 0; y ≥ 0
Subject to:

## Slide 219: Example 1
x
3
0
1
2
y
0
1
2
4
3
Maximize x + y
x + y = 2
Feasible Solution
x + 2 y ≥ 2
y ≤ 4
x ≤ 3
x ≥ 0; y ≥ 0
Subject to:

## Slide 220: Example 1
x
3
0
1
2
y
0
1
2
4
3
Maximize x + y
x + y = 3
x + 2 y ≥ 2
y ≤ 4
x ≤ 3
x ≥ 0; y ≥ 0
Subject to:

## Slide 221: Example 1
x
3
0
1
2
y
0
1
2
4
3
Maximize x + y
x + y = 7
Optimal Solution
x + 2 y ≥ 2
y ≤ 4
x ≤ 3
x ≥ 0; y ≥ 0
Subject to:

## Slide 222: Solving a LP problem (1)
Constraints define a polyhedron in n dimensions
If a solution exists, it will be at an extreme point (vertex) of this polyhedron
Starting from any feasible solution, we can find the optimal solution by following the edges of the polyhedron
Simplex algorithm determines which edge should be followed next

## Slide 223: Which direction?
x
3
0
1
2
y
0
1
2
4
3
Maximize x + y
x + y = 7
Optimal Solution
x + 2 y ≥ 2
y ≤ 4
x ≤ 3
x ≥ 0; y ≥ 0
Subject to:

## Slide 224: 3D Polyhedron

## Slide 225: Solving a LP problem (2)
If a solution exists, the Simplex algorithm will find it
But it could take a long time for a problem with many variables!
  Interior point algorithms

## Slide 226: Interior point methods
Constraints
(edges)
Extreme points
(vertices)
Simplex: search from vertex to vertex along the edges
Interior-point methods: go through the inside of the feasible space

## Slide 227: Conclusions
Robustness of LP is an enormous advantage
  If there is a solution, it will be found
Many non-linear optimization problems are linearized so they can be solved using LP
Very efficient implementation of LP solution algorithms are available in commercial solvers

## Slide 228: Sequential Linear Programming (SLP)
Used if more accuracy is required
Algorithm:
  Linearize
  Find a solution using LP
  Linearize again around the solution
  Repeat until convergence

## Slide 229: Mixed Integer Linear Programming

## Slide 230: LP formulation of Economic Dispatch
A
B
C
L
PA=x1
PAMAX
PB=x2
PBMAX
PC=x3
PCMAX

## Slide 231: LP formulation of Economic Dispatch
Objective function is linear
All constraints are all linear
All variables are real
 Problem can be solved using standard linear programming

## Slide 232: LP formulation of Economic Dispatch
PA=x1
PAMAX
PB=x2
PBMAX
PC=x3
PCMAX
PAMIN
PBMIN
PCMIN

## Slide 233: Can we use LP for unit commitment?
PA=x1
PAMAX
PB=x2
PBMAX
PC=x3
PCMAX
PAMIN
PBMIN
PCMIN

## Slide 234: Can we use LP for unit commitment?
PA=x1
PAMAX
PB=x2
PBMAX
PC=x3
PCMAX
PAMIN
PBMIN
PCMIN
The variables no longer have a continuous domain.
Standard linear programming
is no longer applicable.

## Slide 235: Integer Programming
Integer programming:
  All decision variables are integers
  Special case: binary variables {0,1}
Mixed Integer Programming
  Some decision variables are integer or binary
  Other variables are real
Mixed Integer Linear Programming (MILP)
  Objective function and constraints are linear
Mixed Integer Non-Linear Programming (MINLP)

## Slide 236: Example
Except for the fact that the variables are integer, this looks very much like a linear programming problem.

## Slide 237: Example

## Slide 238: LP Relaxation
The LP solution “relaxes” the constraints that all variables can only take integer values

## Slide 239: LP Relaxation
The relaxed LP solution is always “better” than the solution of original problem!
(Lower objective for minimization problem, higher for maximization)

## Slide 240: Solution of the integer problem
Can we find it by simply “rounding” the LP solution to the nearest integer?

## Slide 241: Integer Programming Example

## Slide 242: Naïve rounding off
-cT
x1
x2
LP solution
IP solution
The optimal integer solution can be far away from the LP solution

## Slide 243: Finding the integer solution
Large number of integer variables
Vast number of possible integer solutions
Need a systematic procedure to search this solution space
Fix the variables to the nearest integer one at a time
“Branch and Bound” algorithm

## Slide 244: Another example
Relaxed LP solution: (1.75, 0.75)

## Slide 245: Branch on x1
Problem 0
Problem 2
Problem 1

## Slide 246: Branch on x1
Problem 2
Problem 1
Solution of Problem 2
Solution of
Problem 1

## Slide 247: Search Tree: first layer
Solution of Problem 1:
x1 integer
x2 real
Not a feasible solution yet
Can still branch on x2
Solution of Problem 2:
x1 & x2 integer
Feasible solution of the original problem
Bound on the optimum
Best solution so far

## Slide 248: Branch on x2
Problem 1
Problem 3
Problem 4

## Slide 249: Branch on x2 for Problem 1
Problem 2
Problem 1
Problem 3
Problem 4
x2 = 2
x2 = 1

## Slide 250: Branch on x2 for Problem 1
Problem 2
Problem 1
Problem 3
Problem 4
x2 = 2
x2 = 1
Solution of
Problem 4
No solution!

## Slide 251: Search Tree: second layer
No solution
No integer solution yet

## Slide 252: Branch and Bound: what next?
No solution
Can’t go any further in this direction
Solution of relaxed problem 4 is bounded by solution of problem 2. No point in going further
Optimal solution

## Slide 253: Comments on Branch and Bound
Search tree gets very big if there are more than a few integer or binary variables
Even with the bounds provided by the relaxed solutions, exploring the tree usually takes a ridiculous amount of time
Clever mathematicians have developed techniques to identify “cuts”
  Constraints based on the structure of the problem that eliminate part of the search tree
  “Branch and Cut” algorithm

## Slide 254: Mixed Integer Linear Programming
Start with linear programming formulation
Use branch and cut algorithm for integer and binary variables
Each node of the search tree involves the solution of an LP problem

## Slide 255: Duality Gap
Finding the optimal solution for a large problem can take too much time even with branch and cut
Best solution of relaxed problem provides a bound on the solution
Duality gap: Difference between best solutions of relaxed problem and actual problem
Stop searching the tree if duality gap is sufficiently small